## Tabelle1
RAW_DATA_STRUCT | RAW_LABEL | POST_LABEL | DESCRIPTION | PRECISION | UNIT | UNCERTAINTY
HardwareData | ID_Xitron_Watts | id_power | Indoor unit power | 0 | W | 0.5% of reading
HardwareData | OD_Xitron_Watts | od_power | Outdoor unit power | 0 | W | 0.5% of reading
HardwareData | OD_Air_AVG_DB(F) | oa_temp | Measured outdoor drybulb temperature | 1 | DEG_F | 0.8
HardwareData | 1722_HMT331_Output1_ODDewF++ | oa_temp_dp | Measured outdoor dewpoint temperature | 1 | DEG_F | 0.7
HardwareData | Exit_TC_Grid_AVG_Temp(F) | sa_temp | Supply air drybulb temperature | 1 | DEG_F | 0.8
HardwareData | CALC_Exit_Dewtem_F | sa_temp_dp | Supply air dewpoint temperature | 1 | DEG_F | 0.7
HardwareData | 1704_VDC_KahnDrybulbF++ | zn_temp | Measured indoor drybulb temperature | 1 | DEG_F | 0.8
HardwareData | 1703_VDC_KahnDewTempF++ | zn_temp_dp | Measured indoor dewpoint temperature | 1 | DEG_F | 0.7
HardwareData | Indoor_Unit_SCFM | sa_flow | Indoor air flowrate at standard air density (0.075 lbm/ft3) in cubic feet per minute | 0 | FT3-PER-MIN | 3% of reading
HardwareData | Active_Baro_Pres(inHg) | local_pres | Zone barometric pressure | 3 | IN_H2O | 0.004
HardwareData | 1712_RotoMass_Massflow_lb/min++ | ref_flow | Measured refrigerant flowrate | 2 | lbm_per_min | 1% of reading
SimData | T_out | oa_temp_sim | Simulated outdoor drybulb temperature | 1 | DEG_F | NA
SimData | NA | oa_temp_dp_sim | Simulated outdoor dewpoint temperature corrected by local barometric pressure | 1 | DEG_F | NA
SimData | T_out | oa_temp_spt_emu | Outdoor drybulb temperature setpoint for outdoor emulation, equivalent to oa_temp_sim | 1 | DEG_F | NA
SimData | NA | oa_temp_dp_spt_emu | Outdoor dewpoint temperature setpoint for outdoor emulation, equivalent to oa_temp_dp_sim | 1 | DEG_F | NA
SimData | Tz_cspt | zn_temp_cspt | Indoor drybulb cooling setpoint | 1 | DEG_F | NA
SimData | Tz_hspt | zn_temp_hspt | Indoor drybulb heating setpoint | 1 | DEG_F | NA
SimData | T_z | zn_temp_sim | Simulated indoor drybulb temperature | 1 | DEG_F | NA
SimData | NA | zn_temp_dp_sim | Simulated indoor dewpoint temperature corrected by local barometric pressure | 1 | DEG_F | NA
SimData | T_z | zn_temp_spt_emu | Indoor drybulb temperature setpoint for indoor emulation, equivalent to zn_temp_sim | 1 | DEG_F | NA
SimData | NA | zn_temp_dp_spt_emu | Indoor dewpoint temperature setpoint for indoor emulation, equivalent to zn_temp_dp_sim | 1 | DEG_F | NA
NA | NA | stat | Status (0 setback, 1 occupied) | 0 | - | NA
NA | NA | stg | Stage (0 off, 1 low speed, 2 high speed) | 0 | - | NA
NA | NA | grid_signal_type | Grid signal type (0 no signal, 1 shedding request, 2 time-of-use by energy use, 3 time-of-use by peak demand) | 0 | - | NA
NA | NA | grid_signal_shed | Grid signal shedding request (0 no request, 1 request) | 0 | - | NA
NA | NA | grid_signal_price | Grid signal time-of-use price | 4 | USD-PER-KiloW-HR or USD-PER-KiloW | NA
NA | NA | occ##_gender | Occupant##'s gender (0 female, 1 male) | 0 | - | NA
NA | NA | occ##_accept_low | Occupant##'s thermal acceptability lower bound | 0 | - | NA
NA | NA | occ##_accept_up | Occupant##'s thermal acceptability upper bound | 0 | - | NA
NA | NA | occ##_zn | Occupant##'s zone | 0 | - | NA
NA | NA | occ##_pres | Occupant##'s presense in the office (0 out of office, 1 in the office) | 0 | - | NA
NA | NA | occ##_loc_x | Occupant##'s location x coordinate in the zone | 4 | M | NA
NA | NA | occ##_loc_y | Occupant ##'s location y coordinate in the zone | 4 | M | NA
NA | NA | occ##_sensation | Occupant ##'s thermal sensation (-3 to 3) | 1 |  | NA
NA | NA | occ##_comfort | Occupant ##'s comfort (-1 cool, 0 neutral, 1 warm) | 0 | - | NA
NA | NA | occ##_met | Occupant##'s metabolic rate | 1 | met | NA
NA | NA | occ##_clo | Occupant ##'s clothing level | 4 | clo | NA
NA | NA | occ##_ph | Occupant##'s personal heater status (0 off, 1 on) | 0 | - | NA
NA | NA | occ##_ph_power | Occupant##'s personal heater power | 0 | W | NA
NA | NA | occ##_pf | Occupant##'s personal fan status (0 off, 1 on) | 0 | - | NA
NA | NA | occ##_pf_power | Occupant##'s personal fan power | 0 | W | NA
NA | NA | occ##_spt | Occupant##'s setpoint change | 0 | DEG_F | NA
NA | NA | occ##_drink | Occupant##'s drinking behavior (-1 cold drink, 0 no drink, 1 hot drink) | 0 | - | NA
NA | NA | occ##_act | Occupant##'s activity level (0 sitting, 1 walking) | 0 | - | NA