## Sheet 1
RAW_DATA_STRUCT | RAW_LABEL | POST_LABEL | DESCRIPTION | PRECISION | UNIT | UNCERTAINTY | NOTES
scaledData2 | oau_out_rtd | oau_out_rtd | Outdoor air temperature | 2 | DEG_F | 0.2
SimData | T_out | oa_temp_sim | Outdoor air temperature (simulated) | 2 | DEG_F | NA
SimData | T_out | oau_t_out_sp_f | Outdoor air temperature setpoint for outdoor temperature emulation, same as oa_temp_sim | 2 | DEG_F | NA
scaledData2 | oau_rh | oau_rh | Outdoor air relative humidity | 0 | PERCENT_RH | 2
SimData | w_out | oa_w_sim | Outdoor air humidity ratio (simulated) | 4 | KiloGM-PER-KiloGM | NA
SimData | w_out | oau_rh_out_sp_per | Outdoor air humidity ratio setpoint for outdoor humidity emulation, same as oa_w_sim | 4 | KiloGM-PER-KiloGM | NA
scaledData2 | indoor_p | indoor_p | Local air pressure | 2 | PSI | 0.2
scaledData2 | ch1_power | ch1_power | Power consumption of Chiller1 | 2 | W | 1 % of reading
scaledData2 | ch1_on | ch1_on | On/off control signal for Chiller1 (0 - off, 1 - on) | 0 | - | NA
scaledData2 | pump1_power | pump1_power | Power consumption of Pump 1 (Chiller 1 water pump) | 2 | W | 1.2 % of reading
scaledData2 | ch1_f_e | ch1_f_e | Flow rate of the PG through the evaporator in Chiller1 | 2 | GAL_US-PER-MIN | 5 % of reading
scaledData2 | ch1_e_in_rtd | ch1_e_in_rtd | Temperature of the PG returning to both Chiller1 and Chiller2 | 2 | DEG_F | 0.21
scaledData2 | ch1_e_out_rtd | ch1_e_out_rtd | Temperature of the PG leaving the evaporator in Chiller1 | 2 | DEG_F | 0.2
processData2 | ch1_t_sp_f | ch1_t_sp_f | Temperature setpoint of the PG leaving the evaporator in Chiller1 | 2 | DEG_F | NA
scaledData2 | ch2_power | ch2_power | Power consumption of Chiller2 | 2 | W | 1 % of reading
scaledData2 | ch2_on | ch2_on | On/off control signal for Chiller2 (0 - off, 1 - on) | 0 | - | NA
scaledData2 | pump2_power | pump2_power | Power consumption of Pump 2 (Chiller 2 water pump) | 2 | W | 2.6 % of reading
scaledData2 | ch2_f_e | ch2_f_e | Flow rate of the PG through the evaporator in Chiller2 | 2 | GAL_US-PER-MIN | 3.5 % of reading
scaledData2 | ch2_e_out_rtd | ch2_e_out_rtd | Temperature of the PG leaving the evaporator in Chiller2 | 2 | DEG_F | 0.2
processData2 | ch2_t_sp_f | ch2_t_sp_f | Temperature setpoint of the PG leaving the evaporator in Chiller2 | 2 | DEG_F | NA
scaledData2 | pump4_power | pump4_power | Power consumption of Pump4 (conderser loop) | 2 | W | 2.47
scaledData2 | pump4_out_rtd | pump4_out_rtd | Temperature downstream of Pump4 | 2 | DEG_F | 0.21
scaledData2 | ch1_f_c | ch1_f_c | Flow rate of the water through the condenser in Chiller1 | 2 | GAL_US-PER-MIN | 0.54
scaledData2 | ch1_c_out_rtd | ch1_c_out_rtd | Temperature of the water leaving the condenser in Chiller1 | 2 | DEG_F | 0.2
scaledData2 | ch2_f_c | ch2_f_c | Flow rate of the water through the condenser in Chiller1 | 2 | GAL_US-PER-MIN | 0.65
scaledData2 | ch2_c_out_rtd | ch2_c_out_rtd | Temperature of the water leaving the condenser in Chiller1 | 2 | DEG_F | 0.2
processData2 | ts_mode | ts_mode | Operating mode of the thermal storage tank (0 - off, 1 - discharge, 2 - charge) | 0 | - | NA
scaledData2 | ts_meter | ts_meter | Ice meter reading of the inventory in the thermal storage tank | 0 | PERCENT | 5
scaledData2 | ts_f | ts_f | Flow rate through the thermal storage tank | 2 | GAL_US-PER-MIN | 1.51 % of reading
scaledData2 | ts_in_rtd | ts_in_rtd | Temperature of the PG entering the thermal storage tank | 2 | DEG_F | 0.2
scaledData2 | ts_out_rtd | ts_out_rtd | Temperature of the PG leaving the thermal storage tank | 2 | DEG_F | 0.2
scaledData2 | pump3_power | pump3_power | Power consumption of Pump 3 (secondary loop pump) | 2 | W | 2.47
scaledData2 | pump3_dp | pump3_dp | Differential pressure across the secondary loop | 2 | PSI | 0.25 % of reading
scaledData2 | pump3_out_rtd | pump3_out_rtd | Temperature fo the PG downstream of Pump3 (temperature of the PG entering the cooling coils in AHU1 and AHU2) | 2 | DEG_F | 0.2
processData2 | sl_vfd_sp_v | sl_vfd_sp_v | Differential pressure setpoint for the secondary loop pump (Pump 3) | 2 | PSI | NA
scaledData2 | sl_f | sl_f | Flow rate in the secondary loop | 2 | GAL_US-PER-MIN | 0.85
scaledData2 | ahu1_f_sa | ahu1_f_sa | Flow rate of the outdoor air in AHU1 | 0 | FT3-PER-MIN | 10 % of reading
processData2 | ahu1_sa_sp_per | ahu1_sa_sp_per | Flow rate setpoint of the outdoor air in AHU1 | 0 | FT3-PER-MIN | NA
scaledData2 | ahu1_f_ra | ahu1_f_ra | Flow rate of the return airin AHU1 | 0 | FT3-PER-MIN | 10 % of reading
scaledData2 | ahu1_p_down | ahu1_p_down | Static pressure downstream of AHU1 | 3 | IN_H2O | 0.008
processData2 | ahu1_fan_sp_inh2o | ahu1_fan_sp_inh2o | Static pressure setpoint for the supply fan in AHU1 | 3 | IN_H2O | NA
scaledData2 | ahu1_t_ra | ahu1_t_ra | Temperature of the return air in AHU1 | 2 | DEG_F | 0.2
scaledData2 | ahu1_in_rtd | ahu1_in_rtd | Temperature of the mixed air at the inlet of AHU1 | 2 | DEG_F | 0.2
scaledData2 | ahu1_cc_rtd | ahu1_cc_rtd | Temperature of the air after the cooling coil in AHU1 | 2 | DEG_F | 0.2
scaledData2 | ahu1_out_rtd | ahu1_out_rtd | Temperature of the supply air downstream of AHU1 | 2 | DEG_F | 0.2
processData2 | ahu1_cc_sp_f | ahu1_cc_sp_f | Setpoint temperature for the supply air downstream of AHU1 | 2 | DEG_F | NA
scaledData2 | ahu1_rh_ra | ahu1_rh_ra | Relative humidity of the return air in AHU1 | 0 | PERCENT_RH | 2
scaledData2 | ahu1_rh_up | ahu1_rh_up | Relative humidity of the mixed air in AHU1 | 0 | PERCENT_RH | 2
scaledData2 | ahu1_rh_down | ahu1_rh_down | Relative humidity of the supply air downstream of AHU1 | 0 | PERCENT_RH | 2
scaledData2 | ahu1_f_cc | ahu1_f_cc | Flow rate of the PG through the cooling coil in AHU1 | 2 | GAL_US-PER-MIN | 0.25 % of reading
scaledData2 | ahu1_cc_out_rtd | ahu1_cc_out_rtd | Temperature of the PG leaving the cooling coil in AHU1 | 2 | DEG_F | 0.2
scaledData2 | v12_pos_c | v12_pos_c | Control signal for the position of Valve12 (vavle of the cooling coil in AHU1) | 2 | V | NA
scaledData2 | v12_pos_fb | v12_pos_fb | Feedback signal for the position of Valve12 (vavle of the cooling coil in AHU1) | 2 | V | NA
scaledData2 | ahu1_on | ahu1_on | On/off control signal for the AHU1 supply fan | 0 | - | NA
scaledData2 | ahu1_fan_power | ahu1_fan_power | Power consumption of the AHU1 supply fan | 2 | W | 2.47
scaledData2 | ahu1_vfd | ahu1_vfd | Speed of the AHU1 supply fan | 0 | HZ | NA
scaledData2 | d6_pos_c | d6_pos_c | Control signal for the position of Damper6 (AHU1 outdoor air damper) | 0 | V | NA
scaledData2 | d6_pos_fb | d6_pos_fb | Feedback signal for the position of Damper6 (AHU1 outdoor air damper) | 0 | V | NA
scaledData2 | d5_pos_c | d5_pos_c | Control signal for the position of Damper5 (AHU1 recirculate air damper) | 0 | V | NA
scaledData2 | d5_pos_fb | d5_pos_fb | Feedback signal for the position of Damper5 (AHU1 recirculate air damper) | 0 | V | NA
scaledData2 | d10_pos_c | d10_pos_c | Control signal for the position of Damper10 (AHU1 exhaust air damper) | 0 | V | NA
scaledData2 | d10_pos_fb | d10_pos_fb | Feedback signal for the position of Damper10 (AHU1 exhaust air damper) | 0 | V | NA
scaledData2 | vav3_f | vav3_f | Airflow rate through VAV3 | 0 | FT3-PER-MIN | 10 % of reading
processData2 | vav3_d_sp | vav3_d_sp | Flow setpont for the PI controller for the damper in VAV3 | 0 | FT3-PER-MIN | NA
scaledData2 | vav3_t_in | vav3_t_in | Temperature of the air upstream of VAV3 | 2 | DEG_F | 0.2
scaledData2 | vav3_out_rtd | vav3_out_rtd | Temperature of the air downstream of VAV3 | 2 | DEG_F | 0.2
scaledData2 | d17_pos_c | d17_pos_c | Control signal for the position of Damper17 (VAV3 damper) | 0 | V | NA
scaledData2 | d17_pos_fb | d17_pos_fb | Feedback signal for the position of Damper17 (VAV3 damper) | 0 | V | NA
scaledData2 | vav3_heat_power | vav3_heat_power | Power consumption of the electric reheat in VAV3 | 2 | W | 2.47
scaledData2 | vav3_heat_c | vav3_heat_c | Control signal for the electric reheat in VAV3 | 0 | V | NA
scaledData2 | zs3_out_rtd | zs3_out_rtd | Temperature of the air downstream of ZN3 (zone temperature) | 2 | DEG_F | 0.2
SimData | T_z1_ahu1 | zn3_temp_sim | Temperature of ZN3 (simulated) | 2 | DEG_F | NA
SimData | T_z1_ahu1 | zs3_qst_sp_f | Temperature setpoint for sensible load control of ZN3, same as zn3_temp_sim | 2 | DEG_F | NA
processData2 | zs3_t_sp_f | zs3_t_sp_f | Temperature setpont for the air leaving ZN3 (zone temperature setpoint) | 2 | DEG_F | NA
scaledData2 | zs3_rh | zs3_rh | Relative humidity of the air downstream of ZN3 (zone relative humidity) | 0 | PERCENT_RH | 2
EPlusOutput | CONFROOM_MID_2 ZN NODE2:System Node Humidity Ratio [kgWater/kgD | zn3_w_sim | Humidity ratio of ZN3 (simulated) | 4 | KiloGM-PER-KiloGM | NA
EPlusOutput | CONFROOM_MID_2 ZN NODE2:System Node Humidity Ratio [kgWater/kgD | zs3_qlrh_sp_per | Humidity ratio setpoint for latent load control of ZN3, same as zn3_w_sim | 4 | KiloGM-PER-KiloGM | NA
scaledData2 | vav4_f | vav4_f | Airflow rate through VAV4 | 0 | FT3-PER-MIN | 10 % of reading
processData2 | vav4_d_sp | vav4_d_sp | Flow setpoint for the PI controller for the damper in VAV4 | 0 | FT3-PER-MIN | NA
scaledData2 | vav4_t_in | vav4_t_in | Temperature of the air upstream of VAV4 | 2 | DEG_F | 0.2
scaledData2 | vav4_out_rtd | vav4_out_rtd | Temperature of the air downstream of VAV4 | 2 | DEG_F | 0.2
scaledData2 | d18_pos_c | d18_pos_c | Control signal for the position of Damper18 (VAV4 damper) | 0 | V | NA
scaledData2 | d18_pos_fb | d18_pos_fb | Feedback signal for the position of Damper18 (VAV4 damper) | 0 | V | NA
scaledData2 | vav4_heat_power | vav4_heat_power | Power consumption of the electric reheat in VAV4 | 2 | W | 2.47
scaledData2 | vav4_heat_c | vav4_heat_c | Control signal for the electric reheat in VAV4 | 0 | V | NA
scaledData2 | zs4_out_rtd | zs4_out_rtd | Temperature of the air downstream of ZN4 (zone temperature) | 2 | DEG_F | 0.2
SimData | T_z2_ahu1 | zn4_temp_sim | Temperature of ZN4 (simulated) | 2 | DEG_F | NA
SimData | T_z2_ahu1 | zs4_qst_sp_f | Temperature setpoint for sensible load control of ZN4, same as zn4_temp_sim | 2 | DEG_F | NA
processData2 | zs4_t_sp_f | zs4_t_sp_f | Temperature setpont for the air leaving ZN4 (zone temperature setpoint) | 2 | DEG_F | NA
scaledData2 | zs4_rh | zs4_rh | Relative humidity of the air downstream of ZN4 (zone relative humidity) | 0 | PERCENT_RH | 2
EPlusOutput | ENCLOSEDOFFICE_MID_2 ZN NODE2:System Node Humidity Ratio [kgWat | zn4_w_sim | Humidity ratio of ZN4 (simulated) | 4 | KiloGM-PER-KiloGM | NA
EPlusOutput | ENCLOSEDOFFICE_MID_2 ZN NODE2:System Node Humidity Ratio [kgWat | zs4_qlrh_sp_per | Humidity ratio setpoint for latent load control of ZN4, same as zn4_w_sim | 4 | KiloGM-PER-KiloGM | NA
scaledData2 | ahu2_f_sa | ahu2_f_sa | Flow rate of the outdoor air in AHU2 | 0 | FT3-PER-MIN | 10 % of reading
processData2 | ahu2_sa_sp_per | ahu2_sa_sp_per | Flow rate setpoint of the outdoor air in AHU2 | 0 | FT3-PER-MIN | NA
scaledData2 | ahu2_f_ra | ahu2_f_ra | Flow rate of the return airin AHU2 | 0 | FT3-PER-MIN | 10 % of reading
scaledData2 | ahu2_p_down | ahu2_p_down | Static pressure downstream of AHU2 | 3 | IN_H2O | 0.008
processData2 | ahu2_fan_sp_inh2o | ahu2_fan_sp_inh2o | Static pressure setpoint for the supply fan in AHU2 | 3 | IN_H2O | NA
scaledData2 | ahu2_t_ra | ahu2_t_ra | Temperature of the return air in AHU2 | 2 | DEG_F | 0.2
scaledData2 | ahu2_in_rtd | ahu2_in_rtd | Temperature of the mixed air at the inlet of AHU2 | 2 | DEG_F | 0.2
scaledData2 | ahu2_cc_rtd | ahu2_cc_rtd | Temperature of the air after the cooling coil in AHU2 | 2 | DEG_F | 0.2
scaledData2 | ahu2_out_rtd | ahu2_out_rtd | Temperature of the supply air downstream of AHU2 | 2 | DEG_F | 0.2
processData2 | ahu2_cc_sp_f | ahu2_cc_sp_f | Setpoint temperature for the supply air downstream of AHU2 | 2 | DEG_F | NA
scaledData2 | ahu2_rh_ra | ahu2_rh_ra | Relative humidity of the return air in AHU2 | 0 | PERCENT_RH | 2
scaledData2 | ahu2_rh_up | ahu2_rh_up | Relative humidity of the mixed air in AHU2 | 0 | PERCENT_RH | 2
scaledData2 | ahu2_rh_down | ahu2_rh_down | Relative humidity of the supply air downstream of AHU2 | 0 | PERCENT_RH | 2
scaledData2 | ahu2_f_cc | ahu2_f_cc | Flow rate of the PG through the cooling coil in AHU2 | 2 | GAL_US-PER-MIN | 0.25 % of reading
scaledData2 | ahu2_cc_out_rtd | ahu2_cc_out_rtd | Temperature of the PG leaving the cooling coil in AHU2 | 2 | DEG_F | 0.2
scaledData2 | v13_pos_c | v13_pos_c | Control signal for the position of Valve13 (vavle of the cooling coil in AHU2) | 0 | V | NA
scaledData2 | v13_pos_fb | v13_pos_fb | Feedback signal for the position of Valve13 (vavle of the cooling coil in AHU2) | 0 | V | NA
scaledData2 | ahu2_on | ahu2_on | On/off control signal for the AHU2 supply fan | 0 | - | NA
scaledData2 | ahu2_fan_power | ahu2_fan_power | Power consumption of the AHU2 supply fan | 2 | W | 2.47
scaledData2 | ahu2_vfd | ahu2_vfd | Speed of the AHU2 supply fan | 0 | Hz | NA
scaledData2 | d7_pos_c | d7_pos_c | Control signal for the position of Damper7 (AHU2 outdoor air damper) | 0 | V | NA
scaledData2 | d7_pos_fb | d7_pos_fb | Feedback signal for the position of Damper7 (AHU2 outdoor air damper) | 0 | V | NA
scaledData2 | d8_pos_c | d8_pos_c | Control signal for the position of Damper8 (AHU2 recirculate air damper) | 0 | V | NA
scaledData2 | d8_pos_fb | d8_pos_fb | Feedback signal for the position of Damper8 (AHU2 recirculate air damper) | 0 | V | NA
scaledData2 | d11_pos_c | d11_pos_c | Control signal for the position of Damper11 (AHU2 exhaust air damper) | 0 | A | NA
scaledData2 | d11_pos_fb | d11_pos_fb | Feedback signal for the position of Damper11 (AHU2 exhaust air damper) | 0 | V | NA
scaledData2 | vav1_f | vav1_f | Airflow rate through VAV1 | 0 | FT3-PER-MIN | 10 % of reading
processData2 | vav1_d_sp | vav1_d_sp | Flow setpont for the PI controller for the damper in VAV1 | 0 | FT3-PER-MIN | NA
scaledData2 | vav1_t_in | vav1_t_in | Temperature of the air upstream of VAV1 | 2 | DEG_F | 0.2
scaledData2 | vav1_out_rtd | vav1_out_rtd | Temperature of the air downstream of VAV1 | 2 | DEG_F | 0.2
scaledData2 | d15_pos_c | d15_pos_c | Control signal for the position of Damper15 (VAV1 damper) | 0 | V | NA
scaledData2 | d15_pos_fb | d15_pos_fb | Feedback signal for the position of Damper15 (VAV1 damper) | 0 | V | NA
scaledData2 | vav1_heat_power | vav1_heat_power | Power consumption of the electric reheat in VAV1 | 2 | W | 2.47
scaledData2 | vav1_heat_c | vav1_heat_c | Control signal for the electric reheat in VAV1 | 0 | V | NA
scaledData2 | zs1_out_rtd | zs1_out_rtd | Temperature of the air downstream of ZN1 (zone temperature) | 2 | DEG_F | 0.2
SimData | T_z1_ahu2 | zn1_temp_sim | Temperature of ZN1 (simulated) | 2 | DEG_F | NA
SimData | T_z1_ahu2 | zs1_qst_sp_f | Temperature setpoint for sensible load control of ZN1, same as zn1_temp_sim | 2 | DEG_F | NA
processData2 | zs1_t_sp_f | zs1_t_sp_f | Temperature setpont for the air leaving ZN1 (zone temperature setpoint) | 2 | DEG_F | NA
scaledData2 | zs1_rh | zs1_rh | Relative humidity of the air downstream of ZN1 (zone relative humidity) | 0 | PERCENT_RH | 2
EPlusOutput | ENCLOSEDOFFICE_MID_5 ZN NODE2:System Node Humidity Ratio [kgWat | zn1_w_sim | Humidity ratio of ZN1 (simulated) | 4 | KiloGM-PER-KiloGM | NA
EPlusOutput | ENCLOSEDOFFICE_MID_5 ZN NODE2:System Node Humidity Ratio [kgWat | zs1_qlrh_sp_per | Humidity ratio setpoint for latent load control of ZN1, same as zn1_w_sim | 4 | KiloGM-PER-KiloGM | NA
scaledData2 | vav2_f | vav2_f | Airflow rate through VAV2 | 0 | FT3-PER-MIN | 10 % of reading
processData2 | vav2_d_sp | vav2_d_sp | Flow setpont for the PI controller for the damper in VAV2 | 0 | FT3-PER-MIN | NA
scaledData2 | vav2_t_in | vav2_t_in | Temperature of the air upstream of VAV2 | 2 | DEG_F | 0.2
scaledData2 | vav2_out_rtd | vav2_out_rtd | Temperature of the air downstream of VAV2 | 2 | DEG_F | 0.2
scaledData2 | d16_pos_c | d16_pos_c | Control signal for the position of Damper16 (VAV2 damper) | 0 | A | NA
scaledData2 | d16_pos_fb | d16_pos_fb | Feedback signal for the position of Damper16 (VAV2 damper) | 0 | A | NA
scaledData2 | vav2_heat_power | vav2_heat_power | Power consumption of the electric reheat in VAV2 | 2 | W | 2.47
scaledData2 | vav2_heat_c | vav2_heat_c | Control signal for the electric reheat in VAV2 | 0 | V | NA
scaledData2 | zs2_out_rtd | zs2_out_rtd | Temperature of the air downstream of ZN2 (zone temperature) | 2 | DEG_F | 0.2
SimData | T_z2_ahu2 | zn2_temp_sim | Temperature of ZN2 (simulated) | 2 | DEG_F | NA
SimData | T_z2_ahu2 | zs2_qst_sp_f | Temperature setpoint for sensible load control of ZN2, same as zn2_temp_sim | 2 | DEG_F | NA
processData2 | zs2_t_sp_f | zs2_t_sp_f | Temperature setpont for the air leaving ZN2 (zone temperature setpoint) | 2 | DEG_F | NA
scaledData2 | zs2_rh | zs2_rh | Relative humidity of the air downstream of ZN2 (zone relative humidity) | 0 | PERCENT_RH | 2
EPlusOutput | OPENOFFICE_MID_1 ZN NODE2:System Node Humidity Ratio [kgWater/k | zn2_w_sim | Humidity ratio of ZN2 (simulated) | 4 | KiloGM-PER-KiloGM | NA
EPlusOutput | OPENOFFICE_MID_1 ZN NODE2:System Node Humidity Ratio [kgWater/k | zs2_qlrh_sp_per | Humidity ratio setpoint for latent load control of ZN2, same as zn2_w_sim | 4 | KiloGM-PER-KiloGM | NA
NA | NA | sys_mode | System mode (0 - setback, 1 - occupied) | 0 | - | NA
NA | NA | grid_signal_type | Type of grid signal (0 - no signal, 1 - shedding request, 2 - time-of-use by energy use, 3 - time-of-use by peak demand, 4- load modulation) | 0 | - | NA
NA | NA | grid_signal_shed | Shedding request (0 - no request, 1 - request) | 0 | - | NA
NA | NA | grid_signal_price | Time-of-use price | 4 | USD-PER-KiloW-HR or USD-PER-KiloW | NA
processData2 | ahu1_fr_frMode | ahu1_fr_frMode | Modulation signal of AHU1 (0 - no modulation, 1 - modulation) | 0 | - | NA
processData2 | ahu1_fr_basePower | ahu1_fr_basePower | Baseline power for AHU1 modulation | 2 | W | NA
processData2 | ahu1_fr_sp_w | ahu1_fr_sp_w | Target delta power for AHU1 modulation | 2 | W | NA
processData2 | ahu2_fr_frMode | ahu2_fr_frMode | Modulation signal of AHU2 (0 - no modulation, 1 - modulation) | 0 | - | NA
processData2 | ahu2_fr_basePower | ahu2_fr_basePower | Baseline power for AHU2 modulation | 2 | W | NA
processData2 | ahu2_fr_sp_w | ahu2_fr_sp_w | Target delta power for AHU2 modulation | 2 | W | NA
NA | NA | occ##_gender | Occupant##'s gender (0 female, 1 male) | 0 | - | NA
NA | NA | occ##_accept_low | Occupant##'s thermal acceptability lower bound | 0 | - | NA
NA | NA | occ##_accept_up | Occupant##'s thermal acceptability upper bound | 0 | - | NA
NA | NA | occ##_zn | Occupant##'s zone | 0 | - | NA
NA | NA | occ##_pres | Occupant##'s presense in the office (0 out of office, 1 in the office) | 0 | - | NA
NA | NA | occ##_loc_x | Occupant##'s location x coordinate in the zone | 4 | m | NA
NA | NA | occ##_loc_y | Occupant ##'s location y coordinate in the zone | 4 | m | NA
NA | NA | occ##_sensation | Occupant ##'s thermal sensation (-3 to 3) | 1 |  | NA
NA | NA | occ##_comfort | Occupant ##'s comfort (-1 cool, 0 neutral, 1 warm) | 0 | - | NA
NA | NA | occ##_met | Occupant##'s metabolic rate | 1 | - | NA
NA | NA | occ##_clo | Occupant ##'s clothing level | 4 | clo | NA
NA | NA | occ##_ph | Occupant##'s personal heater status (0 off, 1 on) | 0 | - | NA
NA | NA | occ##_ph_power | Occupant##'s personal heater power | 0 | W | NA
NA | NA | occ##_pf | Occupant##'s personal fan status (0 off, 1 on) | 0 | - | NA
NA | NA | occ##_pf_power | Occupant##'s personal fan power | 0 | W | NA
NA | NA | occ##_spt | Occupant##'s setpoint change | 0 | DEG_F | NA
NA | NA | occ##_drink | Occupant##'s drinking behavior (-1 cold drink, 0 no drink, 1 hot drink) | 0 | - | NA
NA | NA | occ##_act | Occupant##'s activity level (0 sitting, 1 walking) | 0 | - | NA